## Slide 2: Renewable Power Plants

## Slide 3: Hydro Power Plants
Since the beginning of civilization
Mainly used to generate mechanical driving power
Water has potential energy stored (altitude)
By flowing downwards – converted to kinetic energy
Types
  River power plant
  Storage power plant (incl. pump storage)
  Oceanic power plant

## Slide 4: Overview of hydro power plants

## Slide 5: River Power Plant (dt. Flusskraftwerke)
Also known as run-of-river power plants
Natural flow of water is used to generate electricity
Can be
  Build directly into the river
  Fed by diversion canal
Directly in the river
  Can produce more power
Diversion canal
  Water is separated and led to the power house
  Activities on the river are not influenced

## Slide 6: River Power Plant
Several possibilities to place the power house within the river
  In an artificial bay. Optimal passage of floods
  Two power houses at the river banks. Shared operation
  Foundations conditions better in the river
  Each turbine / generator has its own power house

## Slide 7: River Power Plant
Sediment transportation needs to be considered
River bends
  Inside: silting of sand and gravel
  Outside: rotating currents are removing sediments
Protect inlet channel from silting
  power house at outside
Usually Kaplan turbines used
  work very well up to 25 m fall height

## Slide 8: Cascaded river power plants
Suitable places
  Large quantity of water
  Good head over a large distance
Possible operation modes
  Tipping operation (dt. Kippbetrieb)
  Swell operation (dt Schwellbetrieb)

## Slide 9: Cascaded river power plants
Tipping operation
  All operating at the same time
  Surface of water tips
  Maximum output immediately available
Swell operation
  Sequentially activating energy production
  Water head swells from one plant to another
  Water travels like a wave

## Slide 10: Storage Power Plants
Store potential energy until its usage is needed
  E.g. for medium or peak load hours
May or may not have natural water influx
  long distance pipes used in mountain areas to collect water
Used turbines
  Usually Francis turbines used
    up to 2000 m fall height
    Hugh amount of water
  Occasionally also Pelton turbines
    15 to 500 m fall height
    Work with smaller water flow

## Slide 11: Pump Storage Power Plants
Located at high altitude
Have not enough water influx
Two water reservoirs are build
  One on the bottom of the valley
  One in the mountain
Water in these reservoirs are used to generate electricity
If water is quickly needed, water is send down through the turbine into the lower basin
Water in the lower basin is pumped up when cheap energy is available
Usually operating in a cyclic manner (dt. Wälzbetrieb)

## Slide 12: Pump Storage Power Plant

## Slide 13: Pump Storage Power Plants - Objectives
Upgrading (dt. Veredelung) of base load energy to peak load energy
Use of excess power (dt. Überschussstrom). E.g. from thermal power plants
Cover for peak load
Supports optimization of thermal power operation (Maximize their efficiency)
Supports power frequency control (dt. Leistungsfrequenzregelung) by quickly providing real power
Supports voltage control by providing reactive power (Phase shifting operation)
Supports black start of collapsed grid parts

## Slide 14: Pump Storage Plants
Classification
  Pump storage power plant. Pump sees more than half of the water used by the turbine
  Combined pump storage power plant. Natural influx is dominating

## Slide 15: Pump Storage Plants
HT = HP ; Classical Pump Storage
Natural water supply from several reservoirs
E.g. water collected from 3 side valleys in Galtür-Wirl is pumped to Kops basin HP = 130 m. Connected to Caverne power station in Partenen HT = 800 m
In case of high water
  water is pumped to higher altitude

## Slide 16: Pump Storage
Modern storage pump have a pump head HP of 500 to 800 m
Pump / turbine combinations
  Francis turbines which can be used in both directions
  They are reducing the construction costs by 30%
Pump and turbine separated -> Tandem sets (dt. Tandemsatz)
  Pelton or Francis turbines

## Slide 17: Pump Storage Efficiency
Efficiency – up to 80 %
Efficiency dramatically better than thermal power plants
  Conventional coal power plants 40 to 45%
  Nuclear power plants 30 to 34 %
  Combined cycle gas turbines (CCGT) reaching 60%

## Slide 18: Pump Storage Operation Modes
Cyclic Operation (dt. Wälzbetrieb)
Classical operation mode
  Provide energy for peak load
Doing energy upgrading (dt. Veredelung)
  Use base load energy to pump up the water
Usually the basins are big enough having water for 3 to 5 hours

## Slide 19: Pump Storage Operation Modes
Liberalized electrical market – trade products
  intraday trading
  Increased share of fluctuating energy producers (WT, PV)
Price of peak load has decreased (Classical operation)
  More thermal power plants are able to participate (spinning reserve)
Tertiary control (dt. Minutenreserven)
  Low gas price – pump storage technology is competing with gas turbines
New measures needs to be established to ensure profitable operation
  Capacity market ?

## Slide 20: Pump Storage – Phase shifting operation
Pump storage can be used to provide reactive power (phase shifting)
Reactive power is required for magnetizing
  Transformer
  Induction machines (dt. Asynchronmaschinen)
Big synchronous machines are used
  Manipulating excitation current
  Thus changing the phase angle between voltage and current in the stator windings
During phase shifting
  No mechanical power supplied or consumed via rotor

## Slide 21: Pump Storage Power Plant
Pump mode
Generator mode
Hydraulic short circuit (dt. Hydraulischer Kurzschluss)
A fraction of the water flowing through the turbine during pumping

## Slide 22: Pump Storage Power Plant
Requires
  Regulating pump
  Tandem set
  Low losses in pipes and joints
Advantage
  Entire output power of the plant can be used within seconds for
    Primary control
    Secondary control
    Power frequency support

## Slide 23: Pump Storage Power Plant
Turbine control is used to steer the level of the upper basin (const.; increase, decrease)
Kops II can perform such operation
  3 machines
  Each 150 MW

## Slide 25: Oceanic Power Plants
Great variety of types
  Wave power plants
  Tidal Power plants (dt. Gezeitenkraftwerk)
  Oceanic heat power plant
  Current power plant
Besides tidal turbines, they are all in a stage of technical development

## Slide 26: Wave Power Plant
Mechanically converts wave energy
Wave energy converted to pressure of fluid
Using a pendulum door (left scheme)
Wave water pressed air through a wind propeller (right scheme)

## Slide 27: Tidal Power Plants
Similar constructed like river power plants
Have a dam
Water is stored on one side and during low tide on the other side

## Slide 28: Oceanic heat power plants
Working principle Ocean Thermal Energy Conversion (OTEC)
Temperature differences between surface water and deep water
Difference is used to run a circuit which is used to produce electric energy
No OTEC power plant in commercial use

## Slide 29: Current power plant
Works like under water wind energy plants
Energy of streaming water is converted by the rotor like a wind converter onshore

## Slide 31: Fluid Mechanics
Water (H2O) consists of one oxygen and two hydrogen atoms
Properties needs to be considered when constructing and operating a hydro power plant
Incompressible fluid
  Increasing the pressure of water also increases the pressure to its surroundings
  10 meters head is equal 1 bar
  Water height of 800 m will result in 80 bar at the turbine

## Slide 32: Fluid Mechanics
Density 1 gram per cm3
Increases volume between -4°C to -4°C
  Could destroy machine parts
  Heating required to avoid freezing
Evaporation
  at 1 bar at 100°C
  at 200 mbar already at 18°C
Solvent
  Universal solvent, dissolves more substances then any other liquid
  Results in leaches (dt. Laugen) or acids
  Might cause damage by corrosion

## Slide 33: Flowing velocity
High energy in flowing water
  Sand starts moving at 0.3 m/s
  Smaller gravel: 1 m/s onwards
  Bigger gravel: 1.3 m/s
Past
  River straighten to protect areas from flooding
  Also increased flow velocity –> deepened the river bed
  Lowering the groundwater level
Nowadays
  Countermeasure – dam
  Important argument for enabling hydro power plants

## Slide 34: Flowing velocity
Basic working principle
  potential energy due to its elevation h converted to kinetic energy
Amount of extracted energy
m: mass of water falling
v: velocity
g: accel. due to gravity
h: height
rho: density of water
V: Volume

## Slide 35: Flowing velocity
Previous equation can be re-written as
This equation shows that the velocity increases with the square root of the height.

## Slide 36: Extractable power
Bernoulli’s principle
  Increase of velocity of a fluid causes
  Decrease in pressure or a decrease in the fluids potential energy
  Kinetic energy + pressure energy + potential energy = constant

## Slide 37: Extractable power
Water stored in an open reservoir at a height h has only one component for potential energy
Pressure and kinetic energy are absent
Thus, total power generated from water due its heights:

## Slide 38: Extractable power
This equation shows, power output depends mainly on
  Volume of flow
  Height
Overall efficiency eta is dominated by the generator and turbine

## Slide 39: Calculation example

## Slide 40: Continuity Equation
Continuity equation (dt. Kontinuitätsgleichung) states
  Product of velocity v and cross section area A of flow remains constant
  Incompressible is a property of water
For smaller cross section the water flow velocity increases
For larger cross section the water flow velocity decreases

## Slide 41: Cavitation erosion
Phenomenon cavitation erosion happens close to hydro power plant equipment
Water boils at low pressure.
Causes vapor bubbles
Water with bubbles travel toward low pressure zones
They collapse causing a rush of water fill the empty space and causing dents (dt. dellen) on the equipment

## Slide 42: Cavitation erosion
Occurs under
  high velocity
  low pressure flow conditions
For instance a pump storage power plant
  water is sucked in
    pressure reduced to 20 mbar
    water starts to evaporate at 18 °C
  Pressure starts to rise at the pumping blades and pipes
  Vapor condenses and becomes thiny drops
  This drops have a very high velocity -> cause erosion

## Slide 43: Cavitation erosion
Happens also when within pipes when the cross section A changes and thus also the pressure p
Computer Fluid Dynamics (CFD) software used for designing hydro power plants
In the daily operation cavitation cannot be avoided

## Slide 45: Hydro turbines
Names after their inventors
  Francis turbine
  Pelton turbine
  Kaplan turbine
  https://www.youtube.com/watch?v=k0BLOKEZ3KU

## Slide 46: Francis turbine
James Francis
British-American civil engineer
Invented the Francis turbine 1849
Reaction machine
  water flow changes its momentum
  gives energy to the surface of the turbine blades
  causes change of pressure due to their profile
  https://www.youtube.com/watch?v=3BCiFeykRzo

## Slide 47: Francis turbine
Adjustable blades causing the water flow to enter at Inlet point 2
With an angular momentum in the direction of rotation
The curve shape of the rotor blades force the water to leave at Outlet point 1
The change of angular momentum of the fluid between runner inlet and outlet causes torque on the shaft
Guide vanes (in the stator) are directing the water tangentially to the turbine wheel
90° between inlet and outlet

## Slide 48: Pelton turbine
Lester Allan Pelton (1829 – 1908)
American inventor
Studied working principle during gold rush (mining)
Found out
  Split double cup
  Splitting the jet directly onto the common vane
  stream kinetic energy is captured more efficiently
First turbine 1870
Impulse machine

## Slide 49: Pelton turbine
Circular disk mounted on the rotating shaft or rotor
Disk carries cup shaped blades (called buckets)
Single or multiple nozzles are arranged around the wheel
High speed jets striking the buckets at the splitter in the middle of the bucket
Stream divided into two equal streams
These streams flow along the inner curve
Leave it in a almost opposite directions

## Slide 50: Pelton turbine
The change in momentum due to the loss in velocity and change in direction of the water stream produces an impulse
This impulse generates the torque and causes the shaft rotation
Power generator directly coupled on the same shaft
  constant frequency required
  Servo controlled spear valves (Speer Ventile) are used to adapt the flow rate
Water is nearly incompressible
  most of available energy is extracted at the first stage
  Therefor Pelton turbines have only one stage (Unlike gas turbines)

## Slide 51: Kaplan turbine
https://www.youtube.com/watch?v=0p03UTgpnDU

## Slide 52: Kaplan Turbine
Victor Kaplan
Born 1876 in Mürzzuschlag, Austria
Civil Engineer (dt. Maschinenbau-Ingeneur)
Professorship at the institute of civil engineering in Brno
1912 he published his most notable work: the Kaplan turbine

## Slide 53: Kaplan turbine
Rotor looks like a propeller of a ship
Movable rotor blades
Specially suitable for low heights
Reaction turbine
Can be used horizontally or vertically

## Slide 54: Propeller turbine
Same as Kaplan turbine, but with fixed blades

## Slide 55: Efficiency
Depends on water flow and turbine type
Kaplan and Pelton have high efficiency over a wide range of water flow
Propeller turbines are presenting a distinct optimum

## Slide 57: Biofuels
Derived from vegetable matter
  agriculture
  waste materials
Burning
  wood, dung, ...
Produce electricity in two ways
  Burning in a furnace to produce steam
  used as fuel for ignite engine or gas turbine
  co-fired with coal in large steam power plants

## Slide 58: Solar Energy
Photovoltaic conversion
  thin layer of suitable material (typical silicon)
  Discontinuity in electrochemical potential creates a potential differences
Theoretical efficiency is about 25%
Occupy large areas in order to produce MW outputs

## Slide 60: Wind Power Plants
In recent years the output power increased
  Increasing the rotor size
  1980 – 15 meter
  2005 – 115 meter
Getting taller
Most of the components in the nacelle
  Drive train
  Gear box
  Generator

## Slide 61: Wind Turbine
As the output power increases also the grid connection requirements are increasing
They have to stay connected even during a grid fault
  They have to support the grid
  In early days the simply switched off
  E.g. they have to stay connected during low voltage conditions for up to 150 ms

## Slide 62: Energy conversion
Energy conversion systems
Converting kinetic energy from moving air into mechanical rotation
Most used type
  Three blades
  Horizontal axis (HAWT)
Wind drives the blades
Connected via hub to the slow moving shaft
Over the gear box connected to the fast moving shaft
Drives the rotor of the generator
Connected to the grid

## Slide 63: Mechanical system / Electrical system
Mechanical system and electrical system are influencing each other
Wind is fluctuating, therefore changing conditions are applied to the mechanical structure

## Slide 64: Important components
Rotor blades, aerodynamical brake and hub
Drive train, bearings, break, gearbox, generator
Yaw drive to move the nacelle into the wind
Tower and foundation
Electrical components for control and grid connection

## Slide 65: Aerodynamics
Most WT have two or three bladed horizontal axis
  Two blades
    Easier to assemble
    Have to spin faster
    Higher noise emission
    More mechanical stress (tower shadow)
Rotor is mounted on top
  Wind speeds are higher
  Thus more energy can be extracted

## Slide 66: Aerodynamics
Air velocity V moving through the area A is proportional the air density rho and the third power of the velocity V

## Slide 67: Aerodynamics
Only a part of the energy can be extracted
Described in the model of Albert Betz
  undisturbed air stream in V in front
  after passing the downstream velocity is V-Infinity

## Slide 68: Betz model
Based on the described Betz model
Power extracted from the moving wind is the power within the wind multiplied by the so called Betz coefficient
Power coefficient CP cannot be higher than 16/27
Modern WT get as close as 70 to 80% of the calculated maximum Betz coefficient

## Slide 69: Working principles
Aerodynamic profile
Pressure difference caused by moving the air with different velocities along the surface of the blades
Creates a lifting force
This force accelerated the blades up to a speed three to four times faster than the wind speed
Having the blades connected via hub to the drive train converts the lifting forces to a torque at the drive train.

## Slide 70: Force calculations
Two major approaches
  Actuator disc theory
  Blade element method (BEM)
Actuator Disc Theory
  Area swept by the blades are seen as disk
  Air flow through disk causes an air velocity decrease
  Thus the force at the disc is the velocity drop multiplied by the mass flow rate

## Slide 71: Force calculations
Blade element method (BEM)
Widely used by wind turbine control design
Based on applying aerodynamic forces on axial blade elements
Blade is divided into N number of elements (between 10 – 20)
Forces applied to each element is determined by the lift and drag coefficients
Each single element experiences a different air flow
  different speed rotation Ωr
  different blade profile (cord length c, twist angle gamma)

## Slide 72: Blade element
Upstream point of view
  blades are turning clockwise
Airplane wing like shapes – turning faster then the wind blows
Because air stream velocities moving along the blades surface causing under pressure and thus forces
fLift causes the blade to move
fLift is perpendicular to relative air stream VRel
fDrag is parallel to the relative air stream
Sum of fLift and fDrag can be divided into
  Rotor plane direction fRotor
  Axial direction fThrust

## Slide 73: Aerofoil
Forces fLift and fDrag are depending on
  The air stream velocity Vrel
  Blade shape
  Angle alpha of the airfoil in the air stream.

## Slide 74: Typical airfoil NACA 0012
Lift and drag coefficients of a typical aerofoil
Designed in such a way that between 0 – 10°
  CLift = linear
  CDrag = close to zero

## Slide 75: Mechanical Structure
Lattice tower
Tubular steel tower
Oscillating forces are acting
  Aerodynamic excitations; e.g. tower shadow
  Hydrodynamic excitations; waves at offshore wind turbines
  Operational excitations; caused by pitch or generator controller
  Unbalanced loads; e.g. damaged blade caused by lightning, ice

## Slide 76: Generator
Directly coupled induction generator systems
Doubly fed induction generator systems
Synchronous generator systems
In the past
  Generators directly connected to the grid frequencies
  Called fixed-speed wind turbines
  Reliable, low cost
  Do not adapt to wind variations

## Slide 77: Generators
Variable speed wind turbines
  not directly coupling their rotational frequency to the grid frequency
  Operate the wind turbine always at the most efficient speed
Decoupling via
  Gear box
  Converters
Used generators
  Induction
  Synchronous

## Slide 78: Directly coupled induction generator
Induction generator tied to the grid
Gearbox needed
Constant speed concept

## Slide 79: Doubly fed induction generator (DFIG)
Changeable generator input speeds
  Stator directly connected to the grid
  Rotor field manipulated by an back-to-back converter
  Speed can change between +/- 40 % of the synchronous speed

## Slide 80: Synchronous generator
Full variable speed concept
Decoupling the generator totally from the grid by using a back-to-back inverter
Permanent magnet synchronous generator mostly used
No gear box needed

## Slide 81: Grid connections
Generator voltage 690 V L-L RMS
Connected to the grid via point of common coupling (PCC)
Depending of the output power
  Medium voltage
  High voltage connection

## Slide 82: Grid codes
Connection restrictions defined in the Grid Codes
  Frequency control; Fast output power control
  Voltage control; Reactive power control
  Black start capabilties

## Slide 83: Control
Target
  Maximum energy can be extracted
  Keep rotational speed for each wind speed at is optimum
If the wind gets too strong, two methods to limit power capture
  Pitch control; move blades
  Stall control; blade design